## Slide 1: Joint Optimization of Idle and Cooling Power in Data Centers While Maintaining Response Time
Faraz Ahmad and T. N. Vijaykumar
Purdue University
Presented by: Michael Moeng

## Slide 2: Key Idea
Techniques to reduce idle power rely on shutting down servers
  Concentrate load in a few servers
  Causes hot spots, which increases cooling costs
Techniques to reduce cooling power rely on spreading out load
  Spread load on many servers
  Keeps all servers on at low utilization, which increases idle power
Joint optimization is crucial for reducing overall power

## Slide 3: Outline
Existing techniques
PowerTrade
  Static schemes
  Dynamic scheme
SurgeGuard
Experimental Results

## Slide 4: Idle Power: Spatial Subsetting
Concentrate load in as few servers as possible
Active servers get hotter
  Cooling cost largely dominated by maximum temperature
Response time degrades

## Slide 5: Temperature: Inverse-temperature assignment
Load servers inversely to the temperature of the room
  Example: middle aisle is cooler, so give those servers a higher load
Keeps all servers on, increases idle power

## Slide 6: Data Center Model

## Slide 7: DVFS: Temporal Subsetting
Degrades response time, especially if transition times are slow
Only reduces CPU component of power (about 1/3 of system power)
Future technologies may not even use DVFS to reduce power

## Slide 8: PowerTrade
Define NetPower as:
  powercompute+ poweridle + powercooling
Divide room into zones with similar temperatures properties
  Distribute load across zones
  Distribute load within single zone
  Assume hot, warm, cool zones
Propose 3 policies to distribute load

## Slide 9: PowerTrade-s: load across zones
Static Scheme, assumes knowledge of:
  Zone partitions
  Expected load
Use calibration run

## Slide 10: PowerTrade-s: load across zones
Calibration results in iso-temp ratio
Hot zone kept on standby if possible

## Slide 11: PowerTrade-s: load within a zone
Cool zone:
  Less prone to hot spots
  Use spatial subsetting to reduce idle power
Warm zone:
  Equal load distribution
Hot zone:
  Kept in standby if possible
  Equal load distribution if necessary

## Slide 12: PowerTrade-s: Limitations
Assumes linear relationship between load and temperature
Intra-zone policies do not consider both cooling and idle power
Ignores heat exchange between zones
  Calibration runs each zone in isolation

## Slide 13: PowerTrade-s++
PowerTrade-s assumed linear relationship between load and temperature
Take multiple samples

## Slide 14: PowerTrade-d
Use server groups: ~10 servers
Reduce power by dealing with one group at a time until we reach net power minimum
Compare potential savings from reducing cooling power and reducing idle power
  Largest is selected to reduce net power

## Slide 15: PowerTrade-d: analysis
Do we reach a global minimum?
Cooling and idle power are mostly monotonic
  Single global minimum

## Slide 16: PowerTrade-d: analysis
How fast is convergence?
About 3 steps per hour
  Slow loading changes
  Relatively large groups
How do we deal with groups in data centers that handle multiple services?
Servers in a group must all handle a single service
  Group size << service server requirement

## Slide 17: PowerTrade-d: loading increase
Try to handle new load with existing servers
  Activate more if necessary
  Else: possible temperature savings increases while possible idle savings decreases
Initially start new group, redistribute load according to inverse-temperature assignment
  Measure cooling improvement
  Measure idle power degradation
If net benefit, try activating another group and repeat
Else keep current group count

## Slide 18: PowerTrade-d: loading decrease
Possible temperature savings decrease, but potential idle savings increases
Try deactivating a group, redistribute load
  Measure cooling degradation
  Measure idle improvement
If net benefit, try deactivating another group and repeat

## Slide 19: PowerTrade-d: group selection
Which server group do we choose to (de)activate?
When deactivating servers, select the hottest server group
When activating servers,
  Select the group with the lowest idle power rating (if they differ)
  Select the from cool, warm, then hot zones

## Slide 20: PowerTrade-d: issues
Server wear from repeated on/off cycles
  Try to select from eligible groups in round-robin fashion
Power overhead from activating servers
  Loading changes are infrequent, so this contributes little to total power
Some data centers have frontend/backend servers
  Add state-aware groups?

## Slide 21: SurgeGuard: Maintaining Response Time
Increases in load require servers to transition states, which takes time
Two-tier Scheme:
  Overprovision to handle maximum increase in load during next coarse-grained time interval
  Replenish reserves at finer granularities to handle spikes

## Slide 22: Spatial Subsetting: active servers
Model data center as GI/G/m queue
Allen-Cunneen approximation:

## Slide 23: SurgeGuard: coarse-grained overprovisioning
Given desired response time and load, the number of active servers can be derived
Overprovision by reserving extra servers
  Worst-case increase in load observed so far
  Load change tolerable for power-performance goal
  Authors use only? 10% of data center servers

## Slide 24: SurgeGuard: fine-grained overprovisioning
What if load decreases one interval, but increases in the next?
Run algorithm after each mini-interval (5 min)
  Reserve exceeded in about 0.15% of all 5 minute intervals
Only activate servers for fine-grained overprovisioning
  Prevent server wear

## Slide 25: Experimental Results: Net Power
Simulate a data center with 1120 server blades

## Slide 26: Experimental Results: Net Power
Shows improvement over better of either spatial subsetting or inverse-temperature

## Slide 27: Experimental Results: Net Power Breakdown

## Slide 28: Experimental Results: Temperature Variation

## Slide 29: Experimental Results: Response Time

## Slide 30: Experimental Results: Response Time

## Slide 31: Questions/Comments?